MAMALA BAY STUDY

WASTEWATER MANAGEMENT STRATEGIES

IN AN INTEGRATED COASTAL MANAGEMENT PLAN

FOR MAMALA BAY

PROJECT MB-11A

Principal Investigator:

Donald R.F. Harleman

Consulting Engineer

Massachusetts Institute of Technology

Cambridge, Ma. 02139

Co-Principal Investigators

Susan Murcott and Shawn Morrissey

Consulting Engineers

Massachusetts Institute of Technology

Cambridge, Ma. 02139

March 1996

EXECUTIVE SUMMARY

MB-11A

Wastewater Management Strategies in an Integrated Coastal Management Plan

for Mamala Bay

This report presents the methods and results of the MB-11A project "Wastewater Management Strategies in an Integrated Coastal Management Plan for Mamala Bay." It covers work conducted during the period from June 1993 - March 1996, including 4 field trips to Hawaii of 2 - 6 weeks duration in August 1993, November 1993, June - July, 1994 and March 1995. The report provides descriptions and evaluations of management strategies for Mamala Bay, based on the integrated coastal management methodology.

This report includes a 6-year performance evaluation (Section 4.1). The key result here is that BOD performance at both primary treatment plants has declined in the past several years. Water quality characterization of Sand Island and Honouliuli wastewater treatment plant influent and effluent determined values for soluble COD, sulfate, alkalinity, chloride, salinity, conductivity, nitrogen, phosphorus and a number of other parameters not typically  measured at Hawaii's treatment plants or elsewhere in order to obtain a more complete picture of the wastewater itself (Section 4.2 and 4.3). Extensive work was carried out investigating performance at the existing facilities at Sand Island and Honouliuli and upgrade processes including CEPT and disinfection (Section 4.4 and 4.5). Neither dissolved air flotation (DAF) at Sand Island nor pre-aeration at Honouliuli showed impressive performance. DAF evaluations were based on a comparison to conventional gravitational settling. Pre-aeration evaluations was compared to treatment without pre-aeration.

In contrast, full-scale CEPT tests showed good results at Honouliuli (80% TSS removal, 40% BOD removal) and impressive BOD results at Sand Island (45%-60% removal). Full-scale CEPT TSS results at Sand Island, which averaged about 65% removal, need further verification. There appears to be an analytic or problem with TSS (as well as a measurement problem with sludge solids) that may account for the discrepancy. Sludge quantities were determined at both existing facilities by 2 methods, and sludge quantities for 3 levels of treatment: primary, CEPT, and conventional primary with biological treatment, were computed and compared (Section 4.6).

We investigated disinfection alternatives to chlorination for the wastewater treatment plants, if disinfection is deemed necessary (Section 4.7). UV disinfection using medium pressure mercury lamps is a new technology available to a wastewater treated with CEPT. Transmittance analyses performed on full-scale CEPT-treated effluent samples are in a range appropriate to treatment with this new disinfection technology

Simulation modeling of 3 levels of wastewater treatment: conventional primary, CEPT, and secondary provided information useful to MB-5 in their overall modeling effort (Section 4.8). Results of MB-11's simulation modeling showed that a significant improvement in BOD, TSS and bacterial removal will result using CEPT over conventional primary treatment.

The  "Conclusions" section of this report is comprised of four subsections: a presentation of integrated coastal management, a description of a wide range of management scenarios for the Ala Wai Canal, for non-point sources, and for the municipal wastewater treatment plants at Sand Island and Honouliuli, an evaluation of these management scenarios and  a discussion of experiences with CEPT in San Diego, Hong Kong, and Mexico City.

Recommendations for the protection of Mamala Bay complete the report. The principal recommendations include:

Sand Island Wastewater Treatment

CEPT + UV disinfection;

Honouliuli Wastewater Treatment Plant

CEPT for 25 mgd flow that continues to be discharged through the ocean outfall;

Ala Wai Canal

Non-point source management of the Ala Wai Canal;

Nonpoint Source Management of Kewalo Basin, Ke'ehi-Honolulu Harbor, Pearl Harbor, and the Ewa Plain Watersheds

Source control/pollution prevention;

Boat waste management;

Community-based watershed management program.

TABLE OF CONTENTS

1.    Executive Summary

2.    Introduction

2.1 Scope of Work

2.2 Objectives

2.3 Project Organization

2.4 Regulatory and Legal Background

3.    Methods

3.1 Task Summary

3.2 Task Methodology

3.2.1 Experimental Analyses

3.2.2 Influent Sampling and Characterization

3.3. Data Base Preparation

3.3.1 Performance Data Bases

3.3.2 Simulation Modeling Data Bases

4.    Results

4.1  Treatment Plant Performance Analysis

4.2  Water Quality Characterization

4.2.1 Sand Island

4.2.2 Honouliuli

4.3  Phosphorus and Nitrogen Water Quality Characterization

4.4  Sand Island Treatment Evaluations

4.4.1 Dissolved Air Flotation

4.4.2 Chemically Enhanced Primary Treatment

4.4.3 Treatment of Sludge Recycle Flow

4.5  Honouliuli

4.5.1. Pre-aeration Treatment Efficiency

4.5.2. Chemically Enhanced Primary Treatment

4.6  Sludge Treatment and Disposal Impacts

4.6.1 Mass Balance

4.6.2 Projected Sludge Quantities for Two Treatment Upgrade Alternatives

4.7  Disinfection

4.7.1 White Paper

4.7.2 Current Disinfection Situation at Sand Island and Honouliuli

4.7.3 Federal and State of Hawaii Bacterial Standards

4.7.4 Disinfection Alternatives for Sand Island and Honouliuli WWTPs

4.7.5 UV Disinfection

4.8  Simulation Modeling Results

4.8.1 Wastewater Treatment Plant Simulation Model

4.8.2 Sand Island CEPT Simulation Modeling

4.8.3 Honouliuli CEPT Simulation Modeling

5.    Conclusions

5.1 Integrated Coastal Management

5.2 Description of Management Scenarios

5.2.1 Ala Wai Canal

5.2.2 Non-point Source Management (other than the Ala Wai)

5.2.3 Sand Island and Honouliuli Treatment Plant Upgrade Scenarios

5.3 Evaluation of Management Scenarios

5.3.1 Ala Wai Canal

5.3.2 Non-point Source Management  Scenarios (other than Ala Wai)

5.3.3 Sand Island and Honouliuli Treatment Plant Upgrade Scenarios

5.4 Experience with CEPT at San Diego, Hong Kong and Mexico City

5.4.1 San Diego

5.4.2 Hong Kong

5.4.3 Mexico City

6.    Recommendations

7.    References

8.    Appendices

8.1  Sand Island and Honouliuli Performance Analysis for the Period January 1988 - June 		1993

8.2 Sand Island and Honouliuli Performance Analysis for the Period January 1988 - 		September, 1994.

8.3 Point Source Characterization and Control Options for Mamala Bay -- Special Project 		Report: September 1993 - 1994, January, 1994

8.4 Testing Chemically Enhanced Primary Treatment at Sand Island and Honouliuli 		Wastewater Treatment Plants -- Mamala Bay Study, Special Project February, 		1994

8.5 Laboratory Studies at Honouliuli and Sand Island Treatment Plants and the Ala 		Wai Canal

8.6 Wastewater Treatment Plant Simulation Model

8.7 Disinfection of Wastewater Discharges to Coastal Waters: Current Practices and 		Concerns

FIGURES

Figure 3.1  -  Sand Island WWTP Schematic

Figure 3.2  -  Honouliuli WWTP Schematic

Figure 4.1  -  Sand Island Monthly Average BOD Removal (Jan. 1988 - Sept. 1994)

Figure 4.2  -  Sand Island Monthly Average TSS Removal (Jan. 1988 - Sept. 1994)

Figure 4.3  -  Honouliuli Monthly Average BOD Removal (Jan. 1988 - Sept. 1994)

Figure 4.4  -  Honouliuli Monthly Average TSS Removal (Jan. 1988 - Sept. 1994)

Figure 4.5  -  Honouliuli Daily Average Fecal Coliform Values (Jan. 1992 - Sept. 1994)

Figure 4.6  -  Sand Island Bench Scale Tests  -- TSS % Removal vs. Coagulant dose

Figure 4.7  -  Sand Island Bench Scale Tests -- COD % Removal vs. Coagulant Dose

Figure 4.8  -  Sand Island Bench Scale Tests -- COD % Removal vs. Overflow Rate

Figure 4.9  -  Sand Island COD/BOD Correlation

Figure 4.10 - Sand Island Full Scale CEPT Test -- BOD Results

Figure 4.11 - Sand Island Full-Scale CEPT Test -- TSS Results

Figure 4.12 - Impact of Polymer Aging on COD % Removal

Figure 4.13 - Honouliuli Bench Scale Tests -- TSS % Removal vs. Metal Salt Dose

Figure 4.14 - Honouliuli Bench Scale Tests -- COD % Removal  vs. Coagulant Dose

Figure 4.15 - Honouliuli Bench Scale Tests -- COD % Removal vs. Coagulant Dose

Figure 4.16 - Honouliuli Bench Scale Tests -- COD % Removal vs. Overflow Rate

Figure 4.17 - Sand Island Monthly Average Simulation Modeling Results -- Effluent BOD 		Concentration

Figure 4.18 - Sand Island Monthly Average Simulation Modeling Results -- Effluent TSS 		Concentration

Figure 4.19 - Sand Island Monthly Average Simulation Modeling Results -- Effluent 			Enterococcus Values

Figure 4.20 - Sand Island Monthly Average Simulation Modeling Results -- Effluent Fecal 		Coliform Values

Figure 4.21 - Honouliuli Monthly Average Simulation Modeling Results -- Effluent BOD 		Concentration

Figure 4.22 - Honouliuli Monthly Average Simulation Modeling Results -- Effluent TSS 			Concentration

Figure 4.23 - Honouliuli Monthly Average Simulation Modeling Results -- Effluent 			Enterococcus Values

Figure 4.24 - Honouliuli Monthly Average Simulation Modeling Results -- Effluent Fecal 		Coliform Values

Figure 5.1   - Process of Integrated Coastal Management

LIST OF TABLES

Table 3.1   - Test Parameters for MB-11's Mamala Bay Study

Table 3.2   - Performance Data Base Categories

Table 3.3   - Simulation Modeling Data Base Categories

Table 4.1   - Sand Island Influent and Recycle Wastewater Characteristics

Table 4.2   - Honouliuli Influent and Recycle Wastewater Characteristics

Table 4.3   - Sand Island Phosphorus and Nitrogen Influent and Effluent Data

Table 4.4   - Honouliuli Phosphorus and Nitrogen Influent and Effluent Data

Table 4.5   - Results of Full-Scale CEPT Tests at Honouliuli WWTP

Table 4.6   - Mass Balance Sludge Determination Using Two Methods

Table 4.7   - Sludge Quantity Projections for 2 Treatment Upgrade Alternatives

Table 4.8   - U.V. Transmittance  (%) of in Various Hawaii Waste and Surface Waters

Table 4.9   - Parameters Used in Simulation Model

Table 4.10 - Summary of Sand Island Modeling Results

Table 4.11 - Summary of Honouliuli Modeling Results

Table 5.1   - Comparison of Removal of Pollutants of Concern by Runoff Treatment Practices

Table 5.2   - Capital and O&M Costs of Ala Wai Management Scenarios

Table 5.3   - Comparison of DAF and Conventional Gravity Clarification

Table 5.4   - Estimate of Daily Chemical Cost at Sand Island and Honouliuli

Table 5.5   - Annual O&M Cost for CEPT

Table 5.6   - Advantages and Disadvantages of Chlorine and UV Disinfection

Table 5.7   - Cost Comparison of UV Irradiation vs. Chlorination/Dechlorination

Table 5.8  -  Performance/Cost Comparison of CEPT vs. Secondary Treatment at Sand Island and 		Honouliuli Treatment Plants

Disclaimer: 	The authors of this report have conducted this study in their capacity as individual 		consulting engineers. Although they are affiliated with the Massachusetts Institute 		of Technology (MIT),  the use of the name MIT in connection with this study is 		not permitted.