8.6 
Wastewater Trteatment Plant Simulation Model

Wastewater Treatment Plant Simulation Model

A primary and secondary treatment simulation model was developed (Morrissey, 1992) to predict CEPT and secondary treatment removal efficiencies based on daily influent flow and TSS, BOD, Enterococcus and Fecal Coliform concentrations.

Effluent TSS and BOD Modeling

The period originally adopted for the Mamala Bay project modeling effort was October 1993 through September 1994, and the measured influent and effluent daily averaged values for TSS and BOD were used for the existing conventional primary treatment.

In modeling CEPT effluent TSS and BOD at both facilities, we based our results on measured influent values and constant removal efficiencies of 80% for TSS and 60% for BOD.  These removal effiencies were determined based on bench and full scale tests conducted at both facilities.

For secondary treatment, a generic biological treatment process was assumed; therefore, 85% removal for both TSS and BOD was used.

Effluent Fecal Coliform and Enterococcus Modeling

Both the Sand Island and Honouliuli primary treatment plants measure only the effluent concentrations of Fecal Coliform and Enterococcus.  Therefore, the influent concentrations were calculated.  This calculation was based on information obtained from a number of treatment facilities indicating that indicator organism removal efficiencies are related to BOD removals.  For conventional primary treatment, we assumed a 30% removal of indicator organisms and the influent count was calculated based on effluent values.

Calculation of the CEPT effluent was based on results from other CEPT treatment plants and laboratory studies at each treatment plant.  We assumed a 70% removal of indicator organism using CEPT.

Based on literature values, indicator organism removal for a generic secondary treatment process is about 99%.  99.99% removal of indicator organism can be expected when disinfection is used for either CEPT or secondary treatment.  These values were used in the simulation modeling.

Table 1 summarizes the parameters used in the simulation model.

Table 1

Parameters Used in the Simulation Model

| Treatment Process |  | BOD | TSS | Fecal Coliform | Enterococci |
| --- | --- | --- | --- | --- | --- |
| Raw Influent |  | measured | measured | CPT / 0.7 | CPT / 0.7 |
| CPT Effluent |  | measured | measured | measured | measured |
| CEPT Effluent |  | Raw * 0.4 | Raw * 0.2 | Raw * 0.3 | Raw * 0.3 |
| Secondary Effluent |  | Raw * 0.15 | Raw * 0.15 | Raw * 0.01 | Raw * 0.01 |
| Disinfection Effluent* |  | - | - | Raw*0.0001 | Raw*0.0001 |

Note:	CPT = Conventional Primary Treatment

BOD and TSS are expressed as mg/L

Fecal Coliform and Enterococci are expressed as CFU/100mL

* CEPT of CEPT+Secondary Treatment

Simulation Model Data Bases

Two simulation model data bases have been developed for both the Sand Island and Honouliuli treatment plants. One data base consists of monthly average simulation modeling results from October 1993 through September 1994. The other consists of daily average simulation modeling results from October 1993 through September 1994. Below is Table 2 showing the information headings contained in each of the databases.

Table 2

Simulation Modeling Data Base Categories

| Monthly Average Simulation Modeling Results | Daily Average Simulation Modeling Results |
| --- | --- |
| Date | Date |
| Flow Rate (mgd) | Flow Rate (mgd) |
| Influent BOD Conc (mg/L) | Influent BOD Conc (mg/L) |
| CPT Eff BOD Conc (mg/L) | CPT Eff BOD Conc (mg/L) |
| CEPT Eff BOD Conc (mg/L) | CEPT Eff BOD Conc (mg/L) |
| Secondary Eff BOD Conc (mg/L) | Secondary Eff BOD Conc (mg/L) |
| Influent TSS Conc (mg/L) | Influent TSS Conc (mg/L) |
| CPT Eff TSS Conc (mg/L) | CPT Eff TSS Conc (mg/L) |
| CEPT Eff TSS Conc (mg/L) | CEPT Eff TSS Conc (mg/L) |
| Secondary Eff TSS Conc (mg/L) | Secondary Eff TSS Conc (mg/L) |
| Influent Entero (counts/100mL) | Influent Entero (counts/100mL) |
| CPT Eff Entero (counts/100mL) | CPT Eff Entero (counts/100mL) |
| CEPT Eff Entero (counts/100mL) | CEPT Eff Entero (counts/100mL) |
| Secondary Eff Entero (counts/100mL) | Secondary Eff Entero (counts/100mL) |
| Influent Fecal Coli (counts/100mL) | Influent Fecal Coli (counts/100mL) |
| CPT Eff Fecal Coli (counts/100mL) | CPT Eff Fecal C (counts/100mL) |
| CEPT Eff Fecal Coli (counts/100mL) | CEPT Eff Fecal C (counts/100mL) |
| Secondary Eff Fecal Coli (counts/100mL) | Secondary Eff Fecal Coli (counts/100mL) |

Sand Island CEPT Simulation Modeling

October 1993 and September 1994 was used as the original modeling period selected by the Mamala Bay Commission.  Table 3 summarizes the results of this modeling effort of Sand Island DPW data.

Table 3

Summary of Sand Island Modeling Results

| Process | BOD (mg/L) | TSS (mg/L) | Enterococcus (counts/100mL) | Fecal Coliform (counts/100mL) |
| --- | --- | --- | --- | --- |
| Raw Influent | 136 | 159 | 8.2x105 | 2.1x107 |
| Primary Effluent | 95 | 51 | 5.8x105 | 1.5x107 |
| CEPT Effluent | 54 | 32 | 2.5x105 | 4.4x106 |
| Secondary Effluent | 20 | 24 | 8.2x103 | 1.5x105 |
| Disinfection | - | - | 8.2x101 | 1.5x103 |

Monthly modeling results are shown graphically in Figures 1-4.  Daily modeling results are shown in Figures 5-8.  Figures 1 and 2 indicate that there is a significant difference in BOD and TSS effluent concentration from primary treatment to both CEPT and secondary treatment.  TSS is probably the most important parameter that drives the amount of disinfection dose needed to disinfect and there is little difference between the effluent TSS concentration between CEPT and secondary treatment.  Figures 3 and 4 show the resulting indicator organism counts after each treatment process.  Disinfection assumes that either CEPT or secondary treatment are in use prior to disinfection.

Figures 5 through 8 show the daily variations in effluent concentration and indicate similar results as seen in the monthly figures.  Figures 5 and 6 indicate that there is a significant differnce in BOD effluent concentrations between each treatment option.  TSS is probably the most important parameter that drives the amount of disinfection dose needed to disinfect and there is little difference between the effluent TSS concentration between CEPT and secondary treatment.  Figures 7 and 8 show the resulting indicator organism counts after each treatment process.  Disinfection assumes that either CEPT or secondary treatment are in use prior to disinfection.

Honouliuli CEPT Simulation Modeling

October 1993 and September 1994 was used as the original modeling period selected by the Mamala Bay Commission.  Table 4 summarizes the results of this modeling effort of Honouliuli DPW data.

Table 4

Summary of Honouliuli Modeling Results

| Process | BOD (mg/L) | TSS (mg/L) | Enterococcus (counts/100mL) | Fecal Coliform (counts/100mL) |
| --- | --- | --- | --- | --- |
| Raw Influent | 225 | 223 | 5.3x105 | 3.0x107 |
| Primary Effluent | 153 | 56 | 3.7x105 | 2.1x107 |
| CEPT Effluent | 90 | 45 | 1.6x104 | 8.9x106 |
| Secondary Effluent | 34 | 34 | 5.3x103 | 3.0x105 |
| Disinfection | - | - | 5.3x101 | 3.0x103 |

Monthly modeling results are shown graphically in Figures 9-12.  Daily modeling results are shown in Figures 13-16.  Figures 9 and 10 indicate that there is a significant difference in BOD and TSS effluent concentration from primary treatment to both CEPT and secondary treatment.  Figure 9 also shows that the primary effluent BOD concentration has been steadily increasing over time.  TSS is probably the most important parameter that drives the dose of disinfection needed to disinfect and there is little difference between the effluent TSS concentration between CEPT and secondary treatment.  Figures 11 and 12 show the resulting bacterial counts after each treatment process.  Disinfection assumes that either CEPT or secondary treatment are in use prior to disinfection.

Figures 13 through 16 show the daily variations in effluent concentration and indicate similar results as seen in the monthly figures.

Figure 1 - Sand Island Monthly Average Simulation Modeling Results

Effluent BOD Concentration

Figure 2 - Sand Island Monthly Average Simulation Modeling Results

Effluent TSS Concentration

Figure 3 - Sand Island Monthly Average Simulation Modeling Results

Effluent Enterococcus Values

Figure 4 - Sand Island Monthly Average Simulation Modeling Results

Effluent Fecal Coliform Values

Figure 5 - Sand Island Daily Average Simulation Modeling Results

Effluent BOD Concentration

Figure 6 - Sand Island Daily Average Simulation Modeling Results

Effluent TSS Concentration

Figure 7 - Sand Island Daily Average Simulation Modeling Results

Effluent Enterococcus Values

Figure 8 - Sand Island Daily Average Simulation Modeling Results

Effluent Fecal Coliform Values

Figure 9 - Honouliuli Monthly Average Simulation Modeling Results

Effluent BOD Concentration

Figure 10 - Honouliuli Monthly Average Simulation Modeling Results

Effluent TSS Concentration

Figure 11 - Honouliuli Monthly Average Simulation Modeling Results

Effluent Enterococcus Values

Figure 12 - Honouliuli Monthly Average Simulation Modeling Results

Effluent Fecal Coliform Values

Figure 13 - Honouliuli Daily Average Simulation Modeling Results

Effluent BOD Concentration

Figure 14 - Honouliuli Daily Average Simulation Modeling Results

Effluent TSS Concentration

Figure 15 - Honouliuli Daily Average Simulation Modeling Results

Effluent Enterococcus Values

Figure 16 - Honouliuli Daily Average Simulation Modeling Results

Effluent Fecal Coliform Values

As of May 1995, the Mamala Bay modeling period was changed to April 1994 through Decemeber 1994.  These values were supplied to MB-5.