8.7 Disinfection of Wastewater Discharges to Coastal Waters: Current Practices and Concerns

Sludge Analysis

Introduction

The City and County of Honolulu are currently treating wastewater that enters the Sand Island and Honouliuli treatment plants using conventional primary treatment.  In this section we will evaluate and determine the mass balance at both the Sand Island and Honouliuli treatment plants and then compare this with CEPT and with activated sludge.  In order to evaluate the difference in sludge due to CEPT on a dry basis, we calculated the mass balances of solids at the current treatment facilities, developed equations for the production of CEPT sludge, and then compared the results.  We then estimated the amount of sludge that would be produced with conventional primary treatment plus activated sludge and CEPT plus activated sludge then compared the results.

Methods for Calculating Sludge Mass Balance

A solids mass balance is performed by calculating the dry tons per day (dtpd) of raw primary sludge production by two methods.  These two values are then compared and are useful in verifying the data compiled at the plant.  In the first method, referred to as the TSS method, flow rate and influent and effluent TSS concentrations are used to determine the mass of solids removed.  The second method, or sludge data method, uses data compiled on solids processed at the treatment plants.

Sludge Data Method

This method inventories all the solids processed at the facility.  For example, at the Sand Island treatment plant there are a number of steps in that they take in processing the solids.  Figure 1 shows the solids processing line at the Sand Island treatment plant.  As seen, the solids removed from the system are added together.  All parameters are measured; therefore, the accuracy of this method depends on the quality of the measurements.

TSS Method

The basic assumptions of the TSS method are as follows:

·	The mass of sludge generated equals the mass of solids removed.

·	No biodegradation of the solids takes place.

·	Soluble BOD is not removed

·	Particulate BOD removal has already been incorporated into the TSS measurements.

Sludge production for conventional primary treatment can be calculated using equation 1:

RS = Q * S * 8.34 / 2000							(1)

where:	RS = raw sludge produced (dry tons per day)

Q = wastewater flow rate (mgd)

S = settled solids (mg/l)

Units = 8.34 lb/(mg/l mg), and 2000 lb/ton

For conventional primary treatment, the settled solids (S) is merely the TSS removed during primary sedimentation as shown in equation 2.

S = 1.0 * (TSSrem)								(2)

where:	TSSrem = influent TSS - effluent TSS (mg/l)

The equation is linear with respect to both the flow rate and settled solids.  Therefore, an error in either variable will be directly transferred to the value obtained for the quantity of sludge produced.

Sludge Data Method Applied to Sand Island and Honouliuli

Sand Island

We were provided daily data from March 1992 through February 1993 for the Sand Island plant, the period just prior to the reactivation of the dissolved air flotation system.  A summary of the daily average solids data is shown in Figure 1.  There is an average of 56 dtpd of solids in the influent and 19.4 dtpd in the effluent.  The difference between influent and effluent solids is 56 dtpd minus 19.4 dtpd or 36.6 dtpd.  Therefore, there is 36.6 dtpd minus 24.7 dtpd or 11.9 dtpd not beginning processed at the Sand Island plant.  This represents an error of 33%.  This is a not a good mass balance and has a high error.

An error of 33% is high; therefore, we began calculating mass balances using various measured solids values at the treatment plant.  As seen in Figure 2, the amount of solids leaving the mass balance box is 46.6 dtpd.  If a mass balance is performed around the dashed line box in Figure 2, the mass balance error is reduced to approximately 20%.  A possible explanation for the increased error over the entire system is the error in calculating volatile solids reduction during heat treatment and/or in determining solids content during storage.

Honouliuli

We were provided monthly averaged data from the Honouliuli treatment plant for the entire year of 1993.  The total cake solids processed for the entire year was 6890 dry tons per year.  This is equivalent to 570 dry tons per month or 19 dry tons per day (dtpd).  The average flow to the plant in 1993 was 24.5 mgd with an average TSS concentration of 240 mg/l entering the plant and 62 mg/l leaving the plant.  Hence there is an average of 24.5 dtpd of solids in the influent and 6.3 dtpd in the effluent.  The difference between influent and effluent solids is 24.5 dtpd minus 6.3 dtpd or 18.3 dtpd.  Therefore, there is an excess of 19 dtpd minus 18.3 dtpd or 0.7 dtpd beginning processed at the Honouliuli plant.  This represents an error of only 4%.  This is a good mass balance with a low error.

TSS Method Applied to Sand Island and Honouliuli

Primary Sludge

Table 1 shows the amount of primary sludge produced from March 1992 through February 1993 for both the Sand Island and Honouliuli treatment plant based on the TSS method only.  Sand Island had an average flow of 71 mgd, influent TSS concentration of 190 mg/l and effluent TSS concentration of 56 mg/l during this period.  Honouliuli had an average flow of 24 mgd, influent TSS concentration of 214 mg/l and effluent TSS concentration of 53 mg/l during this period.  This value will be used to project the increase in sludge resulting form CEPT and secondary treatment.

Table 1
Sludge Generation From Sand Island and Honouliuli Treatment Plants

| Treatment Plant | Sludge (dtpd) |
| --- | --- |
| Sand Island | 39.7 |
| Honouliuli | 16.1 |

Based on the optimum concentration of chemicals from the jar testing conducted during the summer and fall of 1993 (Harleman, et.al., 1994) Table 2 for Sand Island and Table 3 for Honouliuli were developed.  In these tables, we assume the same flows and loadings as used to generate Table 1.  The optimum concentrations of each chemical is shown on the table along with the assumed removal efficiencies for both TSS and BOD.  Equations developed above were used to determine sludge quantities.

Table 2
Sludge Generation Comparison for Sand Island

| Chemicals | BOD Rem | TSS Rem | Sludge (TSS Rem) | Sludge (Chem add) | Total Sludge | Ratio (CPT/CEPT) |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 36 | 69 | 39.7 | - | 39.7 | 1.0 |
| 20mg/l FeCl 0.2 Polymer | 44 | 79 | 44.4 | 6.2 | 50.6 | 1.27 |
| 40mg/l FeCl 0.2 Polymer | 48 | 80 | 45.0 | 10.1 | 55.1 | 1.39 |
| 3 mg/l Polymer | 45 | 78 | 43.9 | 0.9 | 44.8 | 1.13 |

There is very little difference in the amount of sludge generated when 3 mg/l of a cationic polymer is added to the wastewater at Sand Island.  However, the increase in TSS and BOD removal is significant.

Table 3
Sludge Generation Comparison for Honouliuli

| Chemicals | BOD Rem | TSS Rem | Sludge (TSS Rem) | Sludge (Chem add) | Total Sludge | Ratio (CPT/CEPT) |
| --- | --- | --- | --- | --- | --- | --- |
| 0 | 41 | 74 | 16.1 | - | 16.1 | 1.0 |
| 20mg/l FeCl 0.2 Polymer | 52 | 77 | 16.5 | 2.1 | 18.6 | 1.16 |
| 40mg/l FeCl 0.2 Polymer | 61 | 91 | 19.5 | 3.4 | 22.9 | 1.42 |

There is a 42% increase in the amount of sludge generated if 40 mg/l of ferric chloride and 0.2 mg/l of an anionic polymer is added to the Honouliuli wastewater.  However, the increase in TSS and BOD removal is significant.

Determination of Secondary Sludge

Based on influent BOD and flow rates at Sand Island and Honouliuli treatment plants (Table 2 and 3) and an estimate of the effluent BOD concentration from conventional primary treatment and CEPT (Harleman, et.al., 1994) we have estimated the sludge production generated were the activated sludge process applied at Sand Island or Honouliuli.  In doing this, we have assumed a biological sludge yield of 0.8 lbs solids / lb of BOD removed regardless of the primary treatment process.  In this analysis, we assumed that the effluent BOD from the activated sludge process is 20 mg/l, again regardless of the primary treatment process.  Table 4 illustrates the amount of sludge generated by each process at the Sand Island plant.  Table 5 illustrates the amount of sludge generated by each process at the Sand Island plant.

Table 4
Sand Island Sludge Comparison (dtpd)

|  | Conv. Prim. Treatment | CEPT (20 mg/l FeCl3 + 0.2 Poly) | CEPT (20 mg/l FeCl3 + 0.2 Poly) | CEPT (3 mg/l Polymer) |
| --- | --- | --- | --- | --- |
| Primary Sludge | 39.7 | 50.6 | 55.1 | 44.8 |
| Secondary Sludge | 20.4 | 17.3 | 15.7 | 16.9 |
| Total Sludge | 60.1 | 67.9 | 70.8 | 61.7 |

As seen, if a secondary treatment process is used there is essentially no difference between a conventional first stage and a CEPT first stage using 3 mg/l of a cationic polymer in terms of total sludge (10.1 dtpd versus 61.7 dtpd).  However, the use of CEPT in the first stage would give a decided cost advantage over a conventional primary first stage because of the reduction in BOD during the primary stage allows for downsizing the secondary system (Karlsson, 1992)

Table 5
Honouliuli Sludge Comparison (dtpd)

|  | Conventional Primary Treatment | CEPT (20 mg/l FeCl3) | CEPT (40 mg/l FeCl3) |
| --- | --- | --- | --- |
| Primary Sludge | 16.1 | 18.6 | 22.9 |
| Secondary Sludge | 8.7 | 6.8 | 5.2 |
| Total Sludge | 24.8 | 25.4 | 28.1 |

Table 5 shows that there is only a slight increase in sludge when CEPT is used instead of conventional primary treatment at the Honouliuli treatment facility.  Again, CEPT would allow downsizing of the secondary system.

Conclusions and Summary

Sludge mass balances were performed for both Sand Island and Honouliuli.  A summary of the results using the sludge data method and the TSS method are summarized below in Table 6.

Table 6
Conventional Primary Sludge (dtpd)

| Method | Sand Island | Honouliuli |
| --- | --- | --- |
| Sludge Data Method | 24.7 | 19 |
| TSS Method | 36.6 | 18.3 |

In Summary:

·	The Honouliuli treatment plant has a good sludge mass balance with an error of 4%.

·	Sand Island treatment plant has a bad sludge mass balance with an error of 33%.

·	Sand Island should have tighter control on their solids measurements.

·	CEPT, using 3 mg/l of a cationic polymer produces an insugnificant additional quantity of sludge compared to conventional primary treatment; however, it allows for downsizing of a biological treament step.

·	CEPT at both Sand Island and Honouliuli significantly improves TSS and BOD removal.

Calculation of Primary and CEPT Sludge Using the TSS Method

The basic assumptions in calculating raw sludge from CEPT are as follows:

·	The mass of sludge generated equals the mass of solids removed + the mass of chemicals added + the mass of total phosphorus removed.

·	No biodegradation of solids takes place.

·	MePO4 (s) is precipitated first, then a combination of MePO4 + Me(OH)3 begins to precipitate according to Figure 1.  This figure shows that as more metal salt is added, less PO43- is associated with the metal and more becomes associated with the hydroxide.

·	Particulate BOD removal has already been incorporated into the TSS measurements.

·	If soluble BOD is removed, usually less than 15% of the incoming SBOD, then an additional term, k(SBODrem), must be added to the sludge equation.  k  = 1.0

·	All polymer added becomes associated with the sludge.

Figure 1:  Soluble P Residual Versus Fe Dose.

Concentration Equivalence for Metal Salts

Primary coagulants can be dosed in terms of mass concentration of the metal salt or the metal or in terms of the molar concentration of the metal.  Given the mass concentration of the metal salt, the mass and molar concentration of the metal can be calculated by using equations (1) and (2), respectively.  Equation (3) illustrates the relationship among the three various concentrations.

Meion = Mesalt * [f * mMeion / mMesalt]					(1)

Memol = [Mesalt / mMeion] * [f*mMeion / mMesalt] = [f*Mesalt] / mMesalt	(2)

Memol = [f * Mesalt] / mMesalt = Meion / mMeion				(3)

where:	Meion = mass concentration of metal (mg/l)

Mesalt = mass concentration of metal salt (mg/l)

Memol = molar concentration of metal (mmole/l)

f = number of moles of the metal ion in the metal salt

m = molecular weight (g/mole)

For example, there is one mole of Fe3+ in a mole of FeCl3 and the molecular weight of Fe3+ is 56 g/mole and FeCl3 is 162 g/mole; therefore, given a mass concentration of 40 mg/l FeCl3 the mass concentration of Fe3+ is 13.8 mg/l and the molar concentration of Fe3+ is 0.25 mmole/l.

Stoichiometry of Metal Salts

Additional sludge generated from chemical addition is due to the improved removal of solids, the formation and removal of chemical solids, and the precipitation and removal of soluble solids.  In calculating sludge generated from chemical addition, it is assumed that the metal reacts with the phosphorus first and the excess metal forms hydroxides as shown in Figure 1.  Below is the stoichiometry for ferric chloride; however, the same process can be developed for any metal salt.

Sludge Generated From Ferric Chloride

Chemical	FeCl3  (Ferric Chloride)

Reactions	Fe3+ + PO43- = FePO4

Fe3+ + 3 OH- = Fe(OH)3

Assumptions	Pin = 4.95 mg/l

Pout = 3.35 mg/l	with no chemical addition (32% removal)

Pout = 1.25 mg/l	with chemical addition (75% removal)

Premoved = 2.1 mg/l	by chemical addition alone

Given		Atomic weight of FeCl3 = 162

Atomic weight of P = 31

Atomic weight of Fe = 56

Atomic weight of FePO4 = 151

Atomic weight of Fe(OH)3 = 107

Sludge Calculation

40 mg/l FeCl3 = 13.8 mg/l Fe3+ = 0.2463 mmoles/l Fe3+

FePO4 produced = 2.1 / 31 = 0.0677 mmoles/l FePO4

Excess Fe3+ = 0.2463 - 0.0677 = 0.1786 mmoles/l		(used to precipitate Fe(OH)3)

Sludge	As FePO4 = 151 . 0.0677 = 10.2 mg/l

As Fe(OH)3 = 107 . 0.1786 = 19.1 mg/l

Total Sludge = 29.3 mg/l due to 40 mg/l of FeCl3

Pounds of sludge produced per pound of FeCl3 = 29.3 / 40 = 0.73

Stoichiometric Equation for Sludge Production using Metal Salts

The stoichiometric equation is obtained by assuming that the addition of the metal salt results first in the formation of MePO4 and then any excess metal will react to form several species of metal hydroxides which are simply represented as Me(OH)3.  This assumption yields equation (4)

CS = mMePO4 [Prem/mP] + mMe(OH)3 [Mesalt(mMe/mMesalt)/mMe - Prem/mP]	(4)

where:	CS = chemical sludge concentration(mg/l)

Me = symbol for metal in metal salt

m = molecular weight

Rearranging equation (4) yields equation (5) below.

CS = [(mMePO4 - mMe(OH)3)/mP] * Prem + [mMe(OH)3 / mMesalt] * Mesalt	(5)

Given the molecular weights of the variables shown in equation 5 the following relationship develops for FeCl3 addition:

CS = [(151g/mole - 107g/mole) / 31g/mole] * Prem + [107g/mole / 162g/mole] * Mesalt

CS = [1.42] * Prem + [0.66] * Mesalt

Sludge Resulting from Polymer Addition

If a polymer is added to the waste stream, it is assumed that 100% of the polymer is tried-up with the solids that settle and no precipitation of the solubles (phosphorus) results from reaction with the polymers.  Therefore, the addition of polymers can be expressed by Cp, the concentration of polymer added (mg/l) to the waste stream.

Sludge Equation

Sludge production for CEPT can be calculated using equation 1 as for conventional primary treatment.  However, for conventional primary treatment, the settled solids (S) are merely the TSS removed during primary sedimentation.  For CEPT the settled solids (S) can be derived based on the stoichiometry of the primary coagulant, the amount of phosphorus and TSS removed, and the amount of polymers added as shown in equation (6).

S = 1.0 * (TSSrem) + F x (Prem) + K * (Conc) + Cp				(6)

where:	Prem = influent phosphorus - effluent phosphorus (mg/l)

F = stoichiometric factor, 1.42 for mono and trivalent metals

2.84 for divalent metals

K = constant, 0.26 for alum, 0.59 for AlCl3, 0.66 for FeCl3

Conc = concentration of metal salt added (mg/l)

TSSrem = influent TSS - effluent TSS (mg/l)

Cp = concentration of polymers added (mg/l)

If only polymers are added (no metal salts) then equation 6 can be expressed as follows:

S = 1.0 * (TSSrem) + Cp							(7)

Sludge Mass Balance

Sludge Data Method = TSS Method

16.96 dtpd + 4.23 dtpd + 3.5 dtpd = 56 dtpd - 19.4 dtpd

24.7 dtpd = 36.6 dtpd

error = 33%

Sludge Mass Balance

Sludge Data Method = TSS Method

25.78 dtpd + 3.5 dtpd = 56 dtpd - 19.4 dtpd

29.3 dtpd = 36.6 dtpd

error = 20%

Figure 1: Sand Island Daily Average Solids Mass Balance for Entire System

Figure 2: Sand Island Daily Average Solids Mass Balance for Partial System