APPENDIX 8.3

POINT SOURCE CHARACTERIZATION

AND CONTROL OPTIONS FOR MAMALA BAY

SPECIAL PROJECT REPORT

SEPTEMBER 1, 1993 - JANUARY 31, 1994

by

Donald R. F. Harleman

Shawn P. Morrissey

Susan E. Murcott

Consulting Engineers

Massachusetts Institute of Technology, Room 48-317

Cambridge, Ma. 02139

TABLE OF CONTENTS

Executive Summary

1.   Introduction

2.   Point Source Characterization

3.   Treatment Plant Performance Analysis

4.   Predicted Future Flows and Loadings

5.   CEPT

6.   Secondary and Tertiary Treatment Alternatives

7.   Sludge Analysis

8.   Simulation Modeling

9.   Ala Wai Canal Data Collection

10. Ala Wai Treatment Options

11. References

FIGURES

1. COD and TSS % Removal at Sand Island WWTP with CEPT

2. COD and TSS % Removal at Honouliuli WWTP with CEPT

TABLES

1. Principal Treatment Plant Point Source Loadings to Mamala Bay

2. Summary of Six-Year Performance Evaluations of Sand Island and Honouliuli Wastewater 	Treatment Plant

3. Honouliuli NPDES Requirements

4. Sand Island NPDES Requirements

5. Ala Wai Canal - Water Quality Data Summary

6. Changes in Sediment Nitrogen with Floating Wetlands

1.0  INTRODUCTION

Integrated Coastal Management (ICM), as proposed in Managing Wastewater in Coastal Urban Areas (National Research Council, 1993), is the contextual structure for all of the Mamala Bay Study Projects now underway. The principal role of the Special Project: Point Source Characterization and Control Options (which is designated here as SP-1) has been to provide engineering information on the major point sources of pollution to Mamala Bay and on treatment technologies and control options to improve these discharges.

The work plan for the SP-1 consisted of nine components, seven of which pertained to the two major municipal wastewater treatment plants (WWTPs): Sand Island WWTP and Honouliuli WWTP, and two of which pertained to the Ala Wai Canal. That work is reported on in chapters 2 - 10.

Chapter 2 gives the loadings to Mamala Bay of the conventional pollutants: TSS, BOD, and FOG from the Sand Island and Honouliuli WWTPs. Chapter 3 summarizes the 1992-1993 treatment plant performance analysis for Sand Island and Honouliuli WWTPs. Chapter 4 provides the projections for predicted future flows and loadings. Chapter 5 summarizes the results of chemically enhanced primary treatment (CEPT) testing at Sand Island and Honouliuli WWTPs. Chapter 6 gives our evaluation of secondary and tertiary alternatives for the two wastewater treatment plants currently under consideration and offers five additional alternatives. Chapter 7 discusses the solids mass balance at the two treatment plants. Chapter 8 is the preliminary work we undertook applying a wastewater treatment process simulation model to predict plant performance, effluent concentration and sludge production. Chapter 9 covers water quality in the Ala Wai Canal, based on our sampling and analysis of dry and wet weather data, and on the  data we assembled from a various other sources.  Chapter 10 includes SP-1's evaluation of the current recommendations for the cleanup of the Ala Wai Canal and offers three additional alternative treatment options for the canal.

2.0  POINT SOURCE CHARACTERIZATION

Three point source discharges have been the principal focus of this investigation: the outfall ocean discharges from the Sand Island and Honouliuli Wastewater Treatment Plants (WWTPs) and the Ala Wai Canal. The water quality characteristics of the Ala Wai Canal are discussed in Chapter 9. The loadings of conventional pollutants contributed from the treatment plant sources, based on daily average data from March 1992 through February 1993, are summarized in Table 1:

Table 1

Principle Treatment Plant Point Source Loadings to Mamala Bay

(March 1992 through February 1993)

| Source | TSS (lb/day) | BOD (lb/day) | FOG (lb/day) |
| --- | --- | --- | --- |
| Sand Island | 33,200 | 62,200 | 13,600 |
| Honouliuli | 10,600 | 25,600 | 6,200 |

In terms of these loadings, both facilities are currently in compliance with their NPDES permits.

Additional key issues relating to point source characterization include the following:

Nutrients: nitrogen and phosphorus are not measured in the influent or effluent of the two treatment plants.  Under their respective NPDES permits, nutrients are measured beyond the zone of initial dilution (ZID).

Nonconventional pollutants: there is limited data available on nonconventional pollutant loadings to Mamala  Bay from these two wastewater treatment plants.

Although chlorination facilities are available at both treatment plants, no disinfection of effluents presently  occurs. Effluent fecal coliform is regularly measured.

3.0  TREATMENT PLANT PERFORMANCE ANALYSIS

The performance of the Sand Island and Honouliuli WWTPs has been investigated and reported on in The City and County of Honolulu Sand Island and Honouliuli Treatment Plants: A Performance Analysis for the Period January 1988 through June 1993 (Morrissey, 1994). The evaluation of monthly data for the six-year period January 1988 through November, 1993 was supplemented by an analysis of daily data at each plant for the eleven-month period January 1992 through November, 1993. A summary of the key results from the six-year evaluation is presented in Table 2 and commented on below:

Table 2

Summary of Six-Year Performance Evaluation

of Sand Island and Honouliuli Wastewater Treatment Plants

|  | Ave. Flow mgd | Max.* Flow mgd | TSS Effl. mg/l | TSS % Removal | BOD Effl. mg/l | BOD % Removal | FOG** Effl. mg/l |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sand Island | 73 | 82 | 61 | 68 | 119 | 27 | 25 |
| Hono- uliuli | 23 | 27 | 55 | 77 | 112 | 47 | 32 |

* Maximum 3-hour flow

** FOG = fats, oil and grease.

Sand Island:

Average daily flow has increased since May, 1992 from 71 to 73 mgd.

Effluent FOG has increased by almost 50% since June 1992.

Influent pH values of 7.3 to 7.5 and high chloride concentrations (2,000 - 3,000 mg/l) indicate the likelihood of sea water intrusion.

Although Sand Island WWTP does not presently have to meet a 30% BOD removal requirement under its two operating permits, it has consistently met this standard                since March, 1992.

Dissolved air flotation (DAF) has done little to improve removals of TSS and BOD.

Honouliuli:

TSS and BOD removals of 74% and 41% respectively are somewhat higher than usual for conventional primary  treatment. This may due to the beneficial effect of the pre-aeration unit.

Effluent TSS and FOG are fairly constant throughout the study period; BOD has increased, as has the average daily flow.

4.0  PREDICTED FUTURE FLOWS AND LOADINGS

Growth projections for the two Honolulu service areas covered by the Sand Island and Honouliuli WWTPs have been provided in the East Mamala Bay Wastewater Facilities Plan Final Environmental Impact Statement (Belt Collins - Hawaii, 1993) and the Secondary Treatment For the Honouliuli Treatment Plant Expansion Unit 1a (GMP Associates, Inc. 1993) :

East Mamala Bay Service Area:

According to the EIR (Belt Collins - Hawaii, 1993), the East Mamala Bay resident population is projected to reach 412,000 by the year 2015, which is an increase of 40% over the current resident population of Oahu. The average daily flow to the Sand Island WWTP is projected to increase from 78 mgd to 86 mgd. (The average daily flow design capacity of the current Sand Island WWTP is 82 mgd). This estimate is based on land use and population projections.

West Mamala Bay Service Area:

Based on the Performance Analysis (Morrissey, 1994) discussed above, the average daily flow to Honouliuli WWTP is currently 25 mgd. The primary treatment facility is designed for an average daily flow of 51 mgd. The planned expansion and improvement of Honouliuli WWTP to serve the population projected for 2005 is based on the 1982 General Plan of the City and County. According to that estimate, the population is expected to increase relative to 1984 levels by over 40% from 190,000 to 269,000. The average flow is projected to increase from 23 mgd to 35 mgd. This projected flow is well within the limits of plant's current capacity; however, Sand Island could not meet its NPDES BOD loading requirement at a daily average flow of 35 mgd.

5.0  CHEMICALLY ENHANCED PRIMARY TREATMENT (CEPT)

Laboratory-scale tests of CEPT were performed at the Sand Island and the Honouliuli WWTPs during September and November, 1993. The purpose of these tests was to determine the efficacy of low dosages of chemical coagulants in improving treatment plant performance. At Sand Island, both settling tests and DAF tests were performed with and without chemicals. Also, water quality analyses were undertaken at both facilities, with particular attention paid to characterization of the plant influent, recycle flow, and influent + recycle. The design and layout of both facilities were evaluated from the point of view of the ability to successfully test and implement CEPT on a full-scale.

The principal finding of the initial six-month study is that CEPT is a relatively simple and cost-effective way of up-grading the effluents and flow capacity of the existing Sand Island and Honouliuli treatment plants. Our prior experience with CEPT at other facilities has shown that bench-scale results are good predictors of full-scale plant performance (Morrissey, S. and Harleman, D., 1992)

Sand Island WWTP:

At Sand Island WWTP, consultants for the City and County of Honolulu have proposed the use of chemical additives and performed bench-scale tests. Construction of facilities to implement "expanded primary" is underway (Towill, 1992). The limited objective of the City and County of Honolulu's expanded primary program is to meet an expected future 30% BOD removal requirement.

The CEPT program we propose has a different objective, that of optimizing the use of coagulant additives to provide a marked improvement in the effluent. Based on our tests at Sand Island, the improvement in COD (about the same for BOD) and TSS removals due to the addition of various coagulants is displayed in Figure 1. By proper choice of primary coagulant and dose it should be possible to increase BOD removal at Sand Island from 30% to 50% and solids removal from 65% to 80%. This improvement in primary treatment plant performance would also result in a significant reduction in the size and cost of secondary treatment in the event that it is needed at Sand Island.

Honouliuli WWTP:

At Honouliuli WWTP, as part of a consent decree, the Hawaii Department of Health will require additional treatment for flows above 25 mgd, which is currently about the daily average flow at the plant (DOH, 1993). To our knowledge, treatment upgrading by chemical additives has not been proposed or studied at Honouliuli WWTP by the City and County of Honolulu. Our bench-scale tests at Honouliuli WWTP of various coagulants and flocculants are shown in Figure 2. By proper choice of additives, it should be possible to increase BOD removal from 40% to 65% and solids removal from 70% to 85%. These are close to secondary effluent standards and would need only a small amount of BOD polishing to meet secondary levels should this be required in the future.

Consultants for the City and County of Honolulu have prepared a facility plan for a 13 mgd secondary treatment plant (GMP Associates Inc., 1993) that does not provide for any down-sizing due to upgrading the primary plant by CEPT.

Chemical Costs and Sludge Production:

The estimated cost of chemical additives to implement CEPT ranges from $70/MG to $185/MG. Assuming an average coagulant cost of $125/MG allows a rough estimate of $3 million per year at Sand Island WWTP and $1 million per year at Honouliuli WWTP. Additional sludge production due to implementing CEPT is a function of the incremental amount of solids removed and the specific nature of the coagulants used. At Sand Island WWTP, sludge production would increase from 40 dry tons per day currently to between 45 and 50 dry tons per day depending on coagulant type and dose. The corresponding increase in sludge production for Honouliuli is from 16 dry tons per day currently to between 20 and 22.5 dry tons per day.

On account of the low dosage needed, all the cationic polymers (synthetic polymers or chitosan) would provide a cost saving in terms of sludge quantity going to incineration and disposal. On the other hand, ferric chloride and anionic polymer would increase phosphorus removal, which would not occur with the cationic polymers.

Full Scale Testing and Implementation:

There is no obstacles in the current design of Sand Island or Honouliuli WWTP to prevent the successful implementation of CEPT at a full-scale. The design feature which allows each plant to split the flow is an advantageous one which would allow full-scale chemical treatment to be tested in parallel with no chemical addition.

6.0  SECONDARY AND TERTIARY TREATMENT ALTERNATIVES

6.1 Honouliuli Wastewater Treatment Plant

NPDES Requirements

The Honouliuli WWTP currently operates under a federal EPA 301(h) waiver which became effective on June 6, 1991 and is valid for 5 years. In addition to this waiver, the State of Hawaii, Department of Health requires that any additional flow to this plant in excess of 25 mgd receive secondary treatment (DOH, 1993).

To comply with its National Pollutant Discharge Elimination System (NPDES) requirements, the Honouliuli WWTP must meet the following monthly and weekly limits:

Table 3

Honouliuli WWTP NPDES Requirements

|  | Loading kg/day (lb/day) Monthly Average | Loading kg/day (lb/day) Weekly Average | Conc. mg/l Monthly Average | Conc. mg/l Weekly Average |
| --- | --- | --- | --- | --- |
| TSS | 9,000 (20,000) | 13,500 (30,000) | 95 | 142 |
| BOD5 | 15,200 (33,500) | 22,800 (50,000) | 160 | 240 |

The on-going changes taking place at the Honouliuli WWTP are effecting NPDES compliance. The recent construction of two new primary clarifiers (bringing the total up to four) has doubled the average daily primary design capacity of the plant from 25 mgd to 51 mgd. At the present average daily flow of 24 mgd, Honouliuli WWTP is meeting its NPDES permit limits. However, with primary treatment only, any additional increments to the plant flow beyond 30 mgd will not be in compliance with the BOD loading limit of the permit. Therefore, in anticipation of projected future flows ranging from 38 to 51 mgd, plans are underway for inflow in excess of 25 mgd to receive secondary treatment.

Secondary Alternatives Under Consideration

The report Secondary Treatment for Honouliuli Wastewater Treatment Plant Expansion Unit 1A (1993), prepared by GMP Associates Inc. for the Division of Wastewater Management, City and County of Honolulu, compares six candidate processes for secondary treatment:

1) Activated sludge;

2) Trickling filter/solids contact;

3) Aerated lagoons;

4) High-rate trickling filter;

5) Rotating biological contractors;

6) Sequencing batch reactors.

Two feasible options: plug-flow activated sludge and trickling filter/solids contact were chosen for comparison, and trickling filter/solids contact was the recommended process. Both options use the same 100 ft. diameter, 16 ft. deep secondary clarifiers. The sizing of the proposed trickling filter/solids contact option is 13 mgd, based on the 2005 design year total plant flow of 38 mgd. Provisions for expansion to treat 26 mgd to secondary levels, based on the 2020 design year plant flow of 51 mgd was also considered. In either case, the original 25 mgd flow would still continue to be treated to a primary level only, and the final effluent would be combined before discharge. This plan will comply with the current 301 (h) permit.

Additional Recommended Alternatives

In addition to the engineering alternatives recommended by GMP Associates, the Special Project team recommends that the following five alternatives not addressed in the Secondary Treatment for Honouliuli Wastewater Treatment Plant Expansion Unit 1A (1993) be taken into consideration in developing management strategies for the Honouliuli WWTP:

1) CEPT;

2) CEPT + down-sized trickling filter/solids contact;

3) CEPT + biofilters (BOD removal);

4) CEPT + biofilters (nutrient removal);

5) Alternatives to chlorine disinfection facilities.

Alternative 1, CEPT, would allow existing plant capacity to be extended, while decreasing effluent concentrations and continuing to meet all NPDES permit limits. It would also allow down-sizing of secondary treatment if and when such treatment becomes necessary (and/or free up one of the four existing primary clarifiers for secondary clarification on account of CEPT's ability to run at higher overflow rates).

Under alternatives 2 - 4, plant inflow receiving treatment with CEPT could be discharged through the ocean outfall, while meeting all NPDES permits limits, and flow receiving secondary or tertiary treatment would be available for reuse. Thus there are two benefits: an improved ocean discharge (at lower cost) and highly treated water available for reuse.

These additional alternatives allow step-wise improvements in treatment effluent such that water reuse options can be seriously considered. It is our estimation that in the medium term, (10 to 20 years), water reuse should be given serious consideration in any treatment upgrade scenarios for Mamala Bay.

6.2 Sand Island Wastewater Treatment Plant

NPDES Requirements

The Sand Island WWTP currently operates under a federal EPA 301(h) waiver which became effective in February, 1990 and is valid for 5 years.  In addition, Sand Island WWTP is not allowed to discharge over 102 mgd for a maximum three-hour period.

To comply with its National Pollutant Discharge Elimination System (NPDES) requirements, the Sand Island WWTP must meet the following monthly and weekly limits:

Table 4

Sand Island WWTP NPDES Requirements

|  | Loading kg/day (lb/day) Monthly Average | Loading kg/day (lb/day) Weekly Average | Conc. mg/l Monthly Average | Conc. mg/l Weekly Average |
| --- | --- | --- | --- | --- |
| TSS | 26,400 (58,200) | 39,600 (87,300) | 90 | 135 |
| BOD5 | 85,000 (187,600) | 127,600 (281,300) | 290 | 435 |

This NPDES permit is up for renewal in February, 1995, and they are anticipating a more stringent 30% TSS and BOD removal requirement. Currently, Sand Island has been meeting the TSS requirement; however, they do not consistently achieve 30% BOD removal.

On-going Changes in 1993 - 1994

Sand Island WWTP is experiencing on-going changes in plant construction and operation while the Mamala Bay Studies are underway. Beginning in March 1993, on account of a comparison of treatment required under the consent Decree, 20% of the plant inflow began receiving treatment by dissolved air flotation (DAF). Between January and April 1994, 50% of plant inflow will be treated by DAF. In addition, "expanded primary" i.e., the use of cationic polymers prior to primary clarification , will be tested in 1994 with the limited objectee of assuring consistent realization of 30% BOD removal (an expected future requirement). The construction of Interim Chemical Treatment Facilities at Sand Island (Job No. W-13-92) is now underway. Expanded primary entails the dosing of 2.5 mg/l cationic polymer into the liquid stream at a point after sludge processing recycle water is combined with the raw influent. We would distinguish this plan of meeting the limited objective of 30% BOD removal, designated "expanded primary," from CEPT, which has the objective of optimizing treatment performance (and achieving an estimated removal of 45% BOD).

GMP Associates Inc. and Carpenter Environmental Associates are the consulting firms charged with comparing primary treatment performance as regards conventional primary settling versus DAF. However, their assessment is blind to the "expanded primary" upgrade. The MIT Special Project team took a comprehensive look at the effect of the four alternatives: conventional settling or DAF, with or without chemicals, with the aim of determining the degree of treatment possible for each of the alternatives. In addition to these on-going 1993 - 1994 changes, secondary treatment planning is underway.

Expanded Primary, Secondary and Tertiary Treatment Options Under Consideration

The most extensive consideration of treatment options for Sand Island is contained in the recently released December 1993 document: East Mamala Bay Wastewater Facilities Plan -- Final Environmental Impact Statement. This work was performed by Belt Collins Hawaii under contract with the City and County of Honolulu, Department of Wastewater Management. The report considers five options:

1) No action;

2) Optimum operation of existing facilities;

3) Expanded primary treatment;

4) Secondary treatment;

5) Eliminate of reduce ocean discharges.

Belt Collins Hawaii recommend two options:

1) Expanded primary;

2) Selector activated sludge or roughing filter/activated sludge.

Additional Recommended Alternatives

As with the GMP Associates Inc. recommendations for Honouliuli WWTP, the Belt Collins Hawaii recommendations are step-wise improvements which would mainly reduce TSS and BOD loadings to Mamala Bay and, to a lesser degree, reduce phosphorus and nitrogen loadings. However, they do not take into account cost-savings from down-sizing of secondary treatment due to CEPT.

On the basis of performance and cost improvements, the Special Project team recommends that several additional alternatives be taken into consideration:

1) CEPT;

2) CEPT + down-sized activated sludge;

3) CEPT + biofilters (BOD removal);

4) CEPT + biofilters (nutrient removal);

5) Alternatives to chlorine disinfection facilities.

The impacts of the improvements of alternatives 1 - 4 have already been discussed (Section 6.1).  A consideration of alternative 5: alternatives to chlorine disinfection would mean that a variety of disinfection technologies would be among the alternative management scenarios if the ecosystem assessments indicate the need for improved disinfection of Mamala Bay.

7.0  SLUDGE ANALYSIS

A solids mass balance was performed by calculating the amount of solids entering and leaving a system. These values should be the same for the system to be in balance. The Special Project team was provided data from both the Sand Island and Honouliuli treatment plants on the solid streams.

7.1 Sand Island Wastewater Treatment Plant:

For Sand Island, there is an average of 56.3 dry tons per day (dtpd) entering the plant and only 44 dtpd leaving the plant (17 dtpd as cake solids, 4.2 volatile solids destroyed i heat treatment, 3.2 dtpd as grit and 16.6 dtpd discharged to Mamala Bay). Therefore, approximately 15 dtpd is unaccounted for. This represents an error of approximately 26%. Enough information was available for us to begin looking at why there may be this error and we began calculating mass balances using various portions of the solids processing stream. A mass balance around the thickeners only results in a 13% error, indicating that there may be error in measurement/calculation of volatile solids reduction  during heat treatment, determination of solid content during storage or in determining cake solids.

7.2 Honouliuli Wastewater Treatment Plant:

For Honouliuli, there is an average of 21.4 dtps entering the plant and approximately 28.7 dtpd leaving the plant (23.4 dtpd as cake and 5.3 dtpd discharged to Mamala Bay). Therefore, there is approximately 7 dtpd excess sludge being accounted for. This represents an error of approximately 33%. Possible reasons for this error may be due to mistakes in determining the incoming load or in determination of solids content of the cake solids.

8.0  WASTEWATER TREATMENT PLANT SIMULATION MODELING

A wastewater treatment process simulation model has been developed at Parsons Laboratory, MIT  that predicts the daily average plant performance, effluent concentration and sludge production from various components within a treatment plant. The model is based on daily variations in influent characteristics and flow patterns and can be used to predict pollutant effluent loadings, how often a pollutant will violate a permit requirement and sludge produced by various treatment options. The model has been set up so that portions of the flow can be diverted around a specific treatment process. For example, in one secondary treatment plant where the model as been calibrated and tested, a scenario was tested that set a maximum flow limit through the secondary system. The model was then able to calculate the effluent quality for this combined primary and secondary flow.

Each treatment process (primary, CEPT, secondary, nutrient removal) can be modelled in two ways. First, performance curves can be developed and calibrated based on actual plant data or from bench-scale/pilot tests. Second, performance can be based on treatment plant theory where various parameters must be specified. These parameters are determined by analytical means at the treatment plant, from bench-scale or pilot tests, or from literature values.

As part of the initial six-month Special Project, the simulation model has been calibrated against data at both the Sand Island and Honouliuli treatment plants. Effluent concentrations of both TSS and BOD were calculated based on performance curves from plant data for January 1988 through February 1992. The daily influent data from March 1992 though 1993 was then used to calculate the effluent results. There was very good correlation between the modelled data and the actual data.

9.0  ALA WAI CANAL WATER QUALITY

Water quality in the Ala Wai Canal was evaluated by the Special Project team during two trips in 1993 under both dry and rainy conditions. Grab samples, collected from along the entire length of the canal, were analyzed for pH, temperature, conductivity, salinity, COD, soluble COD, TSS, turbidity, ammonia, phosphate, alkalinity, chloride and sulfate. This data was supplemented by water column data collected during the summers of 1991 and 1992 by the University of Hawaii team under the direction of Ed Laws, by R. Fujioka of the University of Hawaii, by State of Hawaii, Department of Health monthly field testing between 1991 and 1993, and by information provided by Marty Stevenson (Kinnetic Laboratories) of MB-3.

Table 5 presents a summary of the assembled data. This table shows the range and median value for various water quality parameters.

Table 5

Ala Wai Canal - Water Quality Data Summary

| ITEM | RANGE | MEDIAN | SOURCE |
| --- | --- | --- | --- |
| Dissolved Oxygen (mg/l) | 4.0 - 8.2 (surface) 4.5 - 8.8 (surface) 2.0 - 9.4 (depth) | 5.7 | DOH, 1993 Laws, 1993 |
| COD (mg/l) | 210 - 920 90 - 802 (upper Manoa Valley) | 561235 | MIT, 1993 Yim + Dugan, 1975 |
| sCOD (mg/l) | 300 - 415 | 305 | MIT, 1993 |
| TSS (mg/l) | 32 - 54 | 38 | MIT, 1993 |
| Turbidity (FTU) | 5 - 15 | 7 | MIT, 1993 |
| Conductivity (micromhos/cm) | 0 - 47,000 | 7000 | MIT, 1993 |
| Salinity (ppt) | 0 - 29 3 - 34 | 12.527 | MIT, 1993 DOH, 1993 |
| Chloride (mg/l) | 5,000 - 13,000 | 7000 | MIT, 1993 |
| Total Nitrogen (mg/l) | 0.02 - 1.07 0.52 - 10.76 (upper Manoa Valley) | 0.57 2.21 | DOH, 1993 Yim + Dugan, 1975 |
| NH4 (mg/l) | 0.1 - 2.5 0 - 0.14 | 0.3 0.07 | MIT, 1993 Laws, 1993 |
| Nitrate (mg/l) | 0.05 - 14.5 | 0.4 | Laws, 1993 |
| TKN (mg/l) | < 0.1 - 0.5 0.42 - 10.75 (upper Manoa Valley) | 0.3 2.1 | DOH, 1993 Yim + Dugan, 1975 |
| Total Phosphorus (mg/l) | 0.006 - 0.09 | 0.033 | DOH, 1993 |
| Phosphate (mg/l) | 0.01 - 0.8 0.04 - 0.35 0 - 0.5 | 0.023 0.02 0.13 | DOH, 1993 MIT, 1993 Laws, 1993 |
| Alkalinity (mg/l as CaCO3) | 60 - 120 | 80 | MIT, 1993 |
| SO4 (mg/l) | 300 - 800 | 740 | MIT, 1993 |
| Chlorophyll a (ug/l) | 5 - 1,032 15 - 45 | 65 | DOH, 1993 Laws, 1993 |
| E. Coli (CFU/100 ml) | 8 - 2,720 | 64 | Fujioka, 1993 |
| Fecal Coliform (CFU/100 ml) | 12 - 2,880 4 - 42,000 | 116160 | Fujioka, 1993 DOH, 1993 |
| Enterococcus (CFU/100 ml) | 0 - 260 7- 50,000 | 56144 | Fujioka, 1993 DOH, 1993 |

Based on this summary, plus work by earlier investigators, the chief water quality problems in the Ala Wai Canal include:

low levels of dissolved oxygen in bottom waters;

high levels of organic material;

high levels of nutrients;

high levels of fecal coliform, enterococcus and other bacteria;

high levels of lead and copper;

high levels of pesticides dieldrin, chlordane and heptachlor expoxide;

high sediment levels;

litter and garbage;

strong fresh water-salinity stratification due to sea water intrusion.

Surface water dissolved oxygen levels range from as low as 4.0 to a high of 8.8 mg/l. Surface waters are supersaturated with oxygen during the day and undersaturated at night. Below 3 meters, oxygen concentration drops to as low as 2 mg/l and frequently violate EPA water quality criteria.

High COD concentrations were found by the MIT team, ranging from as low as 210 mg/l in dry weather to as high as 920 mg/l after rain. Assuming an estimated stream flow of 21 mgd (2.9 x 107 m3/yr) (Freeman, 1993), the Ala Wai point source discharge should be considered a major contributor of organic pollution to Mamala Bay.

Total suspended solids concentrations ranging from 32 to 54 mg/l are at about the same level as would be expected from a secondary treatment plant discharge and hence can be considered  comparatively minor issue.

High conductivity values greater than 40,000 micromhos during dry weather indicate the presence of a significant quantity of salt water in the canal. The conductivity data is complemented by the dry weather salinity data, which shows salinity concentrations up to 29 ppt, almost comparable to Mamala Bay sea water.

Nutrient concentrations are extremely high in the Ala Wai Canal. According to the data assembled by Laws et.al. (1993) "in terms of allochthonous nitrogen loading, the Ala Wai Canal appears to be one of the most heavily fertilized estuaries in the world." Components of the nutrient problem include:

eutrophication and increased algal growth;

turbid, murky green appearance;

unpleasant odor probably associated with low dissolved oxygen.

ammonia levels of between 0.1 and 2.5 mg/l are high enough to be toxic to some aquatic animals, including fish.

Nutrient data collected by the Special Project team in 1993 showed levels of ammonia and phosphate at least as high or higher than that obtained by the University of Hawaii team in 1991 and 1992.

The University of Hawaii team analyzed Ala Wai canal water samples for nitrate and silicon and turned up very high concentrations of these constituents, particularly at the head of the canal. Nitrate concentrations as high as 14.5 mg/l and silicon concentrations as high as 7.3 mg/l were detected.

Median values for State of Hawaii, Department of Health data for 1991 - 1993 of 160 CFU/ 100 ml for fecal coliform and of 144 CFU/100 ml for enterococcus in the Ala Wai Canal suggest the possible presence of pathogenic organisms. This could mean that the water is unsafe for body contact and recreational use. The Department of Health uses fecal coliform to evaluate inland waters and enterococcus to evaluate marine waters. Enterococcus is the organism used to evaluate the Ala Wai. The fecal coliform standard is that water shall not exceed 200 CFU/100 ml in 10 or more samples collected during any 30 day period and not more than 10% of samples shall exceed 400 CFU/100 ml. The enterococcus standard requires that 5 samples collected over a 5 - 8 day interval during 30 days shall not exceed 7 CFU/ 100 ml. Of the 160 enterococcus DOH data points, all samples exceed this standard.

10.0  ALA WAI TREATMENT OPTIONS

It has been known for several decades that the Ala Wai Canal is a significant source of organic material, nutrients, toxics, and pathogens. One of the surprising results of our work on pollutant loading to Mamala Bay (Chapter 2)) and on Ala Wai water quality (Chapter 9) is the recognition that the Ala Wai Canal is a source of pollutants to Mamala Bay comparable to the two municipal wastewater treatment plants at Sand Island and Honouliuli. This final section evaluates the existing management and treatment plans under consideration for cleaning up the Ala Wai and offers three in-canal treatment recommendations.

10.1 Existing Plans for Ala Wai Canal Improvement:

The Department of Land and Natural Resources (DLNR) of the State of Hawaii proposes to improve water quality in the Ala Wai Canal to meet standards acceptable for water-based recreational activities. Objectives of DLNR's work include:

1) increasing water flow and circulation in the canal;

2) decreasing pollutants though improved watershed management;

3) establishing routine maintenance practices.

Objective (1) is within the jurisdiction of the Dept. of Land and Natural Resources; Objective (2) will require a joint effort with DOH, City and County of Honolulu, Neighborhood Boards, and other groups. Objective (3) will require a joint effort with Dept. of Land and Natural Resources and the City and County of Honolulu.

DLNR contracted Noda & Associates to study the feasibility of improving water quality in the canal to meet acceptable standards for water recreational activities (Edward K. Noda & Associates Inc., 1992).

Three reports were produced by Noda & Associates Inc:

1) Ala Wai Improvement Feasibility Report (Edward K. Noda and Associates Inc, 		October, 1992)

2) A Management Plan for the Ala Wai Canal Watershed (East- West Center, 		October, 1992)

3) A Maintenance Plan for the Ala Wai Canal (Edward K. Noda and Associates, 		October, 1992)

Noda & Associates investigated two options to increase water flow and circulation:

1) injection of 20 - 30 cfs seawater inflow into the Kapahulu end of the Ala Wai Canal 		through either a submerged or "non-trenched" pipeline;

2) injection of 20 - 30 cfs of groundwater (with salinity and nutrient concentrations 		similar to coastal seawater) from 5 deep wells drilled to depths of 250 feet in the 		golf course bordering the canal.

The second option -- the deep groundwater supply system -- was recommended by Noda & Associates.

In addition, Noda & Associates subcontracted activities for controlling nonpoint pollution through watershed management to the East-West Center (Fox, J., and Freeman, W., 1992). Recommended community-based watershed management activities include:

cleaning up litter and debris from streambanks and streets;

reducing erosion rates through improved enforcement of grading permit regulations;

expanding hazardous waste and toxic substance collection and disposal activities;

controlling pesticides and heavy metals.

10.2 Assessment of Watershed Management Plan:

The East-West Center watershed management plan would likely make important strides in cleaning up litter and garbage dumping through its community-based activities and holds the promise of reducing pesticides and metals via the expansion of the hazardous waste collection programs and controlling high sediment levels though enforcement of existing pollution control ordinances. We endorse the recommendations of the East-West Center watershed management plan. Yet even with the complete success of the proposed watershed management plan, it is likely that nutrients, bacteria, some metals, pesticides and possible pathogens will remain problematic. A watershed management plan will be an effective pollution prevention approach to limit future inputs. However, given the past history of abuse and degradation of the Ala Wai Canal, various treatment alternatives are also needed to clean it up.

10.3 Proposal of In-Canal Treatment Alternatives:

To the end of cleaning up the Ala Wai Canal in conjunction with a proactive watershed management plan, we have considered three additional treatment alternatives besides deep well seawater injection and flushing recommended by Noda & Associates (referred to below as Alternative 1). The complete list of  treatment alternatives includes:

Alternative 1: Flushing

Alternative 2: Low-Flow Groundwater Injection + Chemical  Coagulation + Submerged 			Weir

Alternative 3: Constructed Floating Wetlands

Alternative 4: In-Canal Oxygenation

The next sections will assess of the pros and cons of Alternative 1, and then describe and evaluate Alternatives 2 - 4.

10.4 Assessment of Alternative 1:

The idea of flushing the canal with seawater to reduce plankton concentrations was first proposed in 1976 (Cox, D., and Miller, J., 1976). Noda & Associates' stated purpose in recommending the injection of 20 - 30 cfs of groundwater from deep wells is  "to achieve the objective of water clarity." The underlying intention is to flush the nutrients from the Ala Wai into Mamala Bay, reducing the residence time of those nutrients in the canal. They expect this will limit phytoplankton growth, measured as chlorophyll a.

Yet based on the work of their subcontractors from the East-West Center, Noda & Associates recognize that "the limiting factor to algae growth [in the canal] is not nutrients but light" (Fox, J. and Freeman, W., 1992). They go on to state that nutrient reduction "is not likely to have a significant effect on algae growth in the Ala Wai" (Fox, J. and Freeman, W., 1992). In the face of this evidence, it would appear that increasing canal water clarity would stimulate algal growth. Apparently Noda and Associates believe this would be offset by reducing the residence time in the canal by flushing. The proposed injection flow rate of 20 - 30 cfs ranges from 66% to 100% of the average natural flow of the Ala Wai. In any event, the underlying result will be to flush nutrients, coliforms, and other material from the canal. Thus while the intended improvement in water clarity will be accomplished, eutrophication and other pollution problems will not be treated but rather shifted from the Ala Wai Canal to Waikiki Beach and Mamala Bay. Noda & Associates maintain that nutrients can easily be assimilated into the Bay without causing problems (Noda, 1994).

We believe that there is short-sightedness in an engineering solution that does not look to the effects of shifting nutrients and pollutants from the Ala Wai Canal to the Waikiki Beach area specifically and Mamala Bay more generally.

In addition, there are confusing statements as to the source of nutrients in the Ala Wai. According to the research of Laws et.al. (1993) "inputs to the canal are virtually all derived from land run-off."  According to the research by OI Consultants as part of the Noda & Associates feasibility study, a large component of the nutrient load to the Ala Wai Canal is from groundwater contributions directly to the canal itself and/or to the Manoa-Palolo Drainage Canal. This confusion as to the pollutant and nutrient sources must be addressed before any treatment alternative is finalized.

10.5 Alternative 2 - Low-Flow Groundwater Injection + Chemical Coagulation + Submerged Weir:

Technology Description:

Alternative 2 is comprised of the two components:

1) injection of 5 to 10 cfs of groundwater from deep wells with chemical coagulant 	addition using either ferric chloride or the natural cationic polymer chitosan                  	(depending on pollutant removal/sludge production objectives);

2) construction of a submerged weir at the Ala Moana end of the canal to restrict salt 	water intrusion.

Objectives:

The objective of this treatment alternative is to remove, by augmented sedimentation, about 50% to 60% of the oxygen demanding material measured as COD, to remove about 75% of suspended solids and turbidity, and to reduce the amount of fecal bacteria and other problematic microorganisms present in the canal. Depending on coagulant selection, about 70% of phosphorus could also be removed. The choice of ferric chloride would significantly reduce phosphorus as well as control odor problems due to the production of H2S in the oxygen-poor portion of the canal; the choice of chitosan would contribute only slightly to the buildup of bottom sediments. The purpose of a submerged weir at the Ala Moana end of the canal is to limit seawater intrusion and increase circulation of freshwater in the canal. Under present conditions it is probable that a salt water wedge is present in the canal and this contributes to low dissolved oxygen in the bottom waters.

Assessment:

The advantages of Alternative 2 are that it limits the transport of pollutants from the Ala Wai to the Waikiki Beach area and Mamala Bay. It treats potentially pathogenic organisms in-situ, rather than flushing them into the Bay. The addition of ferric chloride would reduce or eliminate offensive odors. This alternative could reduce phosphorus, depending on chemical coagulant selection. Either ferric chloride or chitosan would remove > 50% of metals. Reduced sea water intrusion due to the submerged weir would result in improved vertical mixing. Augmented settling would mean the build-up of sludge on the bottom of the canal and this would require dredging or pumping on a regular basis. It is noted that the Ala Wai Canal was originally designed to serve as a sediment deposition basin and plans are underway to dredge the canal in 1994.

10.6 Alternative 3 - Constructed Floating Wetlands:

Description:

As discussed in the innovative technologies section of Managing Wastewater in Coastal Urban Areas (1993) (the innovative technology section was authored by the MIT Special Project team), natural wetland treatment systems represent one family of important innovative treatment technologies. Wetlands treatment systems can be of natural origin or constructed. Constructed wetlands may be comprised of predominantly rooted or floating aquatic species. And the wetlands construction itself may be either a permanent, affixed system or a floating raft system. We recommend consideration of a constructed floating raft system. This alternative represents an in-situ ecological remediation approach to treating the Ala Wai canal.

The advantages of a floating raft system for the Ala Wai Canal are several:

a floated raft system could be moved to sites where treatment is most needed;

rafts could be added (or removed) incrementally as needed;

rafts could be removed in the event of boat races, hurricanes, etc.

plants from the raft could be readily harvested;

rafts would not infringe on costly real estate adjacent to the Ala Wai.

Objectives:

The major objectives of a constructed, floating wetlands system are to remove both nitrogen and phosphorus in-situ, without flushing those nutrients into the Bay. A constructed floating wetlands system would remove various metals and toxics organics, as well as pathogenic organisms.

Nitrogen Removal:

Nitrogen is removed in a constructed wetlands system by a number of mechanisms including: uptake and subsequent harvesting of wetlands plants, volatilization of ammonia, bacterial nitrification/denitrification, sedimentation, adsorption on clay sediment particles. Of these mechanisms, bacterial nitrification/ denitrification has the greatest removal potential (Stowell, 1981). A constructed floating wetlands systems was installed in a eutrophic Cape Cod pond (Flax Pond) in June 1990. Table 6 compares sediment nitrogen data in June 1990 to June 1993 after three years of treatment with the floating raft wetlands system:

Table 6

Changes in Sediment Nitrogen with Floating Wetlands

|  | June 1990 | June 1993 | % Change |
| --- | --- | --- | --- |
| Organic and Ammonia Nitrogen (mg/kg) East End (ave 3 stations) West End (ave 4 stations) | 10,267 9,128 | 9,343 3,448 | -10 -62 |
| Ammonia (mg/kg) East End (ave 3 stations) West End (ave 4 stations) | 714 378 | 28 26 | -96 -92 |
| Nitrates (mg/kg) East End (ave 3 stations) West End (ave 4 stations) | 8.1 8.0 | 0.87 0.30 | -89 -96 |

(Todd, J. and Josephson, B., 1993)

These results were obtained from the use of a single 20' x 27' floating raft in a 15 acre pond. The Ala Wai Canal covers approximately 52 acres and would potentially require several floating rafts.

Dissolved Oxygen:

Between 1990 and 1992 dissolved oxygen on Flax Pond's bottom had dropped to critical lows and key biological processes had been arrested. By 1993, the pond had crossed a threshold and become aerobic across the bottom (Todd, J. and Josephson, B., 1993). This improvement in dissolved oxygen concentration is illustrated in Figures 3 and 4.

Fecal Coliform Removal:

Wetlands have been shown to effectively remove fecal coliforms (Gearheart, 1985; Gersberg, 1984). The mechanisms for removal have been suggested to be flocculation, sedimentation, adsorption, temperature ingestion, and denaturing (oxidation-reduction potential, UV light, etc.).

Metals Removal:

Metals are removed in constructed wetlands by plant uptake, chemical precipitation and ion exchange with and adsorption to settled clay and inorganic compounds.

Assessment:

Advantages of a Constructed Wetlands Scheme:

In-situ removal of nutrients, metals, pathogens, toxic organics;

Increased dissolved oxygen;

Ability to harvest wetlands plants;

Partial restoration of the Ala Wai Canal's original character as a wetlands system;

Increased opportunity for study of and habitat for native Hawaiian wetlands species;

Potential for increasing bird and other wildlife species  in the canal area;

Attraction and educational value for Waikiki tourists;

Opportunity for educational programs and research activities by area students at all grade levels.

Disadvantages of a Constructed Wetlands Scheme:

Possible interference with boating activities;

Possibility of vandalism.

10.7 Alternative 4 - In-Canal Oxygenation:

Description:

In-canal oxygenation can take one of two forms:

fine bubble oxygenation;

large bubble aeration.

Fine bubble oxygenation (with air or oxygen) is undertaken for the purpose of increasing dissolved oxygen levels; large bubble aeration is done expressly for the purpose of improving circulation (exchanging poorer quality bottom water with better quality surface water).

Objectives:

In-canal fine-bubble oxygenation would have the effect of increasing the redox potential of the upper layer of sediments in the Ala Wai and eliminate the occasional odor problem currently associated with the canal. It would probably increase the catabolism of the organic matter in the sediments (Laws, 1993). fine bubble oxygenation would contribute to nitrification.  Large bubble aeration would increase circulation.

Assessment:

The advantages of Alternative 4 are that it is a cost-effective solution which does not require an on-site operator. This is another in-situ solution that will not flush nutrients and pollutants from the canal into the bay.

A disadvantage of this alternative is the possibility of the diffuser clogging with phytoplankton or sediments. However, experience with continuous flow systems (see attached Water Environment & Technology article) show success in preventing clogging. Also, the possibility that bubble aeration may not be efficient in shallow water needs further investigation.

10.8 Combining Alternatives:

We have proposed three additional treatment alternatives in addition to the Noda & Associates Inc. deep well/flushing recommendation. These alternatives, including the Noda & Associates Inc. alternative, are not mutually exclusive. Although some of these treatment alternatives achieve similar objectives (eg. a submerged weir and large bubble aeration both are for the purpose of improving circulation), consideration can and should be given to the possibility of combining alternatives and/or incrementally initiating alternatives. For example, a prototype floating raft could be implemented in conjunction with a single deep well in conjunction with in-canal aeration of the upstream end of the canal. Other combinations are possible and should be explored once the key objectives for the cleanup of the Ala Wai Canal are clearly enunciated as part of an overall integrated coastal management plan for Mamala Bay.

11.0  REFERENCES

Belt Collins - Hawaii, 1993. East Mamala Bay Wastewater Facilities Plan -- Final Environmental Impact Statement. Prepared for the City and County of Honolulu, Honolulu, Hi. December, 1993.

City and County of Honolulu. 1993. East Mamala Bay Wastewater Facilities Plan -- Final Environmental Impact Statement. December, 1993.

City and County of Honolulu. 1993. Secondary Treatment For the 	Honouliuli Treatment Plant Expansion Unit 1a. January, 1993.

Cox, D., and Miller, J. Improvement of the Ala Wai Canal. Final Report. Environmental Center, University of Hawaii,  Honolulu, Hi. December 31, 1876.

Freeman, W. 1993. "Revised Total Maximum Daily Load Estimates for Six Water Quality Limited Segments, Island of Oahu, Hawaii." East-West Center. Honolulu, Hi.

Fox, J., and Freeman, W. Management Plan for the Ala Wai Canal. A report prepared for Edward K. Noda & Associates Inc. East-West Center, Program on the Environment. October, 1992.

Fujioka, R. 1993. unpublished data for 9/8/93.

Gearheart, R.M., Williams, J., Holbrook, H., and Ives, M. "City of Arcata March Pilot Project Wetland Bacteria Speciation  and Harvesting Effects on Effluent Quality." in Proceedings        of a Conference on Wetlands for Wastewater Treatment and Resource Enhancement. Humboldt State University, Arcata, Ca,  August 2 - 4, 1988.

Gersberg, R. M. , Elkins, B.V. and Goldman, C.R. "Wastewater Treatment by Artificial Wetlands." Water Science & 	Technology. Vol. 17. 1984.

GMP Associates Inc. 1993. Secondary Treatment For the Honouliuli  Treatment Plant Expansion Unit 1a. 100% Submittal. Prepared for the City and County of Honolulu. Honolulu, Hi. April, 1993.

Laws, E. 1992. Unpublished data from 1992 summer sampling period.

Laws, E.; Hiraoka, J.; Mura, M.; Puna, B.; Rust, T.; Vink, S.; Yamamura, C. 1993. Impact of Land Runoff on Water Quality in an Hawaiian Estuary. forthcoming publication in Pacific Science.

Laws, E., Dominador, D., Hiayama, J., Hokama, M., Kim, K., Li, 	D., Minami, S., and Morales, C. "Hypereutrophication of the Ala Wai Canal, Oahu, Hawaii: Prospects for Cleanup." Pacific Science. vol. 47. no.1 1993.

Morrissey, S. and Harleman, D. 1992. "Retrofitting Conventional 	Primary Treatment Plants for Chemically Enhanced Primary Treatment in the USA." in Chemical Water and Wastewater Treatment II. Proceedings of the Fifth Gothenburg Symposium. ed. by H. Hahn and R. Klute. Springer-Verlag.

Noda, E. 1994. Personal communication.

Noda & Associates Inc.. Draft Environmental Assessment: Ala Wai Canal Improvement. Honolulu, Hi. November, 1992.

State of Hawaii. 1991. The Population of Hawaii, 1990. Statistical Report 219. Department of Business, Economic Development and Tourism.

State of Hawaii,  Department of Health (DOH). Consent Order.  Docket No 89-CW-EOW-6. June 23, 1993.

State of Hawaii, Department of Health (DOH). Unpublished ambient water quality data for 1991 - 1993 provided by Terry Teruya. Honolulu, Hi.

Stevenson, M. 1994. Personal communication.

Stowell, R., Ludwig, R., Colt, J., and Tchobanoglous, G. "Concepts in Aquatic Treatment System Design." Journal of 	the Environmental Engineering Division, Proceedings of the American Society of Civil Engineers. Vol. 107. No. EE5. October, 1981.

Todd, J. and Josephson, B. "The Rebirth of Flax Pond."  Annals of Earth. Volume XI. Number 3., November 3, 1993.

Towill Corporation. 1992. Sand Island Wastewater Treatment Plant - Unit 1, Phase 2A, Interim Chemical Treatment Facilities. Job No W13-92. Honolulu, Hi.

Towill Corporation. 1975. Sand Island Sewage Treatment Plant and Ocean Outfall. Sewage Treatment Plant Phase II. C-75-10-7818. Job No. S3-74.

Yim, S. and Dugan, G. 1975. Quality and Quantity of Nonpoint Pollution Sources in Rural Surface Water Runoff on Oahu, Hawaii. Technical Report No. 93. OWRT Project No. A-044-HI.