 SEQ CHAPTER \h \r 1
Item: Battery Enclosure

Manuf/Model: Hutton Power Systems, 2BSOL Aluminum Vented Enclosure

Description: 

The enclosure is vented for convective air circulation.  It is seam welded and polyester powder coated 5052-H32 aluminum alloy for durability.  Designed to meet or exceed industry standards: UL50 type 3R and Nema type 3R.  It accommodates two 100 Amp-hour batteries plus the electrical outlet, power strip, low voltage disconnect, and charger.

How is it installed?:

The enclosure is mounted to 2” Diameter six-foot long aluminum pipe.  The aluminum pipe is installed at minimum of 3 feet deep in a 2’ x 2’ x 3’ deep poured concrete block.  The box is grounded via 4 gauge solid copper wire to a 8-foot grounding rod.

